|  | 584SV Series Frequency Inverter - HA463660 |  |
| --- | --- | --- |
|  | Chapter | 11 |
|  | Technical Specifications |  |
|  | Contents Page |  |

- Environmental Details

- Mechanical Details

- Electrical Ratings - Power Circuit (constant torque)

- Electrical Ratings - Power Circuit (quadratic torque)

- EMC Compliance

- External AC Supply (RFI) Filters and AC Line Chokes

- AC Line Choke Specification

- External AC Supply (RFI) Filter Specification

- Brake Unit Rating

- Main Cooling Fan and Supply Requirements

- Supply Harmonic Analysis

# Technical Specifications

The main Product Manual details the technical specification of the control circuits, protection circuits, diagnostics and I/O.

| ### Environmental Details |  |
| --- | --- |
| Humidity (max.) | 85% relative humidity at 40°C non-condensing |
| Altitude | Above 1000m derate 1% per 100m, |
| Atmosphere | Non flammable, non corrosive and dust free |
| Operating temperature range | 0°C to 40°C (Constant torque mode) 0°C to 40°C (Quadratic torque mode) |
| Storage temperature | Minimum -25°C to maximum +55°C |
| Transport temperature | Minimum -25°C to maximum +70°C |
| Climatic Conditions | Class 3k3 as defined by EN50178 (1997) |
| Pollution Degree | 2 |
| Installation / Overvoltage Category | 3 |

| ### Mechanical Details |  |  |
| --- | --- | --- |
| 584SV Type | Detail | Description |
| 8, 9 & 10 | Mounting Orientation | Vertical |
| 8, 9 & 10 | Power Terminations | 3-phase supply and output terminals: Bus-bars with 2 off M12 holes, 25mm separation. 2 off M12 bolt, nut and washer supplied. Tightening torque 97Nm (71.5 lb-ft) Protective Earth terminals: 4 off M10 bolts with conical washers - supplied loose Tightening torque 55Nm (40.5 lb-ft) DC link terminals: Bus-bars with 2 off M12 holes, 35mm separation. Designed to accept semiconductor fuses directly mounted on terminals (eg. Gould Sawmut A100P) 2 off M12 bolt, nut and washer supplied. Tightening torque 97Nm (71.5 lb-ft) Dynamic Brake terminal: Bus-bars with 2 off M12 holes, 44mm separation. 2 off M12 bolt, nut and washer supplied. Tightening torque 97Nm (71.5 lb-ft) |
| 8, 9 & 10 | Control Terminations | Removable screw connectors for 0.75mm2 wire (18 AWG). Terminals will accept up to 1.5mm2 wire (16 AWG). Tightening torque 0.6Nm (0.4lb-ft) |
| 8 | Weight | 100kg (108kg including DB unit) |
|  | Dimensions | Refer to drawing HG463009G003 at the back of this book |
| 9 | Weight | 125kg (138kg including DB unit) |
|  | Dimensions | Refer to drawing HG463009G002 at the back of this book |
| 10 | Weight | 160kg (176kg including DB unit) |
|  | Dimensions | Refer to drawing HG463009G001 at the back of this book |

| ### Electrical Ratings - Power Circuit (constant torque) See the following Notes 1 and 2. |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 584SV Type | Type 8 |  |  |  | Type 9 |  |  |  | Type 10 |  |  |
| Input Voltage |  | 380V to 460V *4 ±10%, 50/60Hz |  |  |  |  |  |  |  |  |  |
| Product Code Block 2 | 0900 |  | 1100 | 1320 |  | 1600 | 1800 | 2000 |  | 2500 | 2800 |
| Nominal Motor Power (kW) @ 380V | 90 |  | 110 | 132 |  | 160 | 180 | 200 |  | 250 | 280 |
| Nominal Motor Power (kW) @ 415/440V | 90 |  | 110 | 150 |  | 185 | 200 | 220 |  | 280 | 315 |
| Motor Power (Hp) @ 460V (as specified within NEC/NFPA-70) | 150 |  | 150 | 200 |  | 250 | 300 | 300 |  | 400 | 450 |
| Output Current (A) | 180 |  | 216 | 250 |  | 316 | 361 | 375 |  | 480 | 520 |
| Input Current (A) * 1 & 2 | 180 |  | 220 | 260 |  | 320 | 360 | 400 |  | 490 | 550 |
| Fundamental Input Power Factor |  | 0.95 |  |  |  |  |  |  |  |  |  |
| Input Bridge I²t |  | 245 000 A²s |  |  | 813 000 A²s |  |  |  |  |  |  |
| Fuse Rating/Circuit Breaker *3 (A) | 200 |  | 250 | 300 |  | 350 | 400 | 450 |  | 550 | 600 |
| Approx. loss @ 3kHz (kW) | 2.4 |  | 2.9 | 3.5 |  | 4.3 | 4.8 | 5.4 |  | 6.7 | 7.5 |
| Switching Frequency |  | 3kHz |  |  |  |  |  |  |  |  |  |
| Output Voltage (max) |  | Input Voltage |  |  |  |  |  |  |  |  |  |
| Output Overload |  | 150% for 60 seconds |  |  |  |  |  |  |  |  |  |
| Output Frequency |  | 0 to 120Hz |  |  |  |  |  |  |  |  |  |
| Fan Inlet temperature Range |  | 0 to 40°C |  |  |  |  |  |  |  |  |  |
| IP Rating |  | IP20 Enclosure, IP00 Power Terminals |  |  |  |  |  |  |  |  |  |
| Earth Leakage Current |  | >>100mA. Product must be permanently earthed |  |  |  |  |  |  |  |  |  |

| ### Electrical Ratings - Power Circuit (quadratic torque) See the following Notes 1 and 2. |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 584SV Type | Type 8 |  |  |  |  | Type 9 |  |  |  | Type 10 |  |
| Input Voltage |  | 380V to 460V *4 ±10%, 50/60Hz |  |  |  |  |  |  |  |  |  |
| Product Code Block 2 | 0900 |  | 1100 | 1320 | 1600 |  | 1800 | 2000 | 2500 |  | 2800 |
| Nominal Motor Power (kW) @ 380V | 110 |  | 132 | 150 | 200 |  | 220 | 250 | 300 |  | 315 |
| Nominal Motor Power (kW) @ 415/440V | 110 |  | 150 | 150 | 225 |  | 250 | 280 | 315 |  | 355 |
| Motor Power (Hp) @ 460V (as specified within NEC/NFPA-70) | 150 |  | 200 | 250 | 300 |  | 350 | 400 | 450 |  | 500 |
| Output Current (A) | 216 |  | 260 | 302 | 377 |  | 420 | 480 | 545 |  | 595 |
| Input Current (A) *1 & 2 | 220 |  | 260 | 300 | 400 |  | 430 | 490 | 590 |  | 620 |
| Fundamental Input Power Factor |  | 0.95 |  |  |  |  |  |  |  |  |  |
| Input Bridge I²t |  | 245 000 A²s |  |  |  | 813 000 A²s |  |  |  |  |  |
| Fuse Rating/Circuit Breaker *3 (A) | 250 |  | 300 | 350 | 450 |  | 450 | 550 | 650 |  | 650 |
| Approx. loss @ 3kHz (kW) | 2.9 |  | 3.5 | 4.2 | 5.1 |  | 5.6 | 6.9 | 7.6 |  | 8.6 |
| Switching Frequency |  | 3kHz |  |  |  |  |  |  |  |  |  |
| Output Voltage (max) |  | Input Voltage |  |  |  |  |  |  |  |  |  |
| Output Overload |  | 110% for 10 seconds |  |  |  |  |  |  |  |  |  |
| Output Frequency |  | 0 to 120Hz |  |  |  |  |  |  |  |  |  |
| Fan Inlet temperature Range |  | 0 to 40°C |  |  |  |  |  |  |  |  |  |
| IP Rating |  | IP20 Enclosure, IP00 Power Terminals. |  |  |  |  |  |  |  |  |  |
| Earth Leakage Current |  | >>100mA. Product must be permanently earthed |  |  |  |  |  |  |  |  |  |

- 1: 3% line impedance MUST be provided for each module, and is assumed in the quoted input current values. Failure to do so will severely curtail DC link capacitor lifetime and could result in damage to the input bridge

2: Input current quoted is for 380V supply at the maximum output motor power. Motor efficiency of 93% is assumed.

3: Short circuit protection Semiconductor Fuses should be installed in the 3-phase supply to the drive module to protect the input bridge.  Circuit breakers or HRC fuses will not protect the input bridge.

4: Suitable for earth referenced (TN) and non earth referenced (IT) supplies.

| ### EMC Compliance Type 8, 9 and 10 Inverters with the option to be ‘CE’ marked meet the following EMC emission limits provided they are installed in accordance with the EMC installation instructions, with the specified EMC filters and line chokes as shown in the “External AC Supply (RFI) Filters and AC Line Chokes” table. * 3kHz switching frequency, 300 metres screened motor cable. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Port | Phenomenon | Basic Standard | Level | Generic Standard |
| Enclosure Port | Radiated | EN55011 (1991) | Class A (cubicle mount) | EN50081-2 (1994) |
| AC Power Port | Conducted (with specified filter) | EN55011 (1991) | Class A (upto 300m screened motor cable) | EN50081-2 (1994) |
| AC Power Port | Conducted (no filter) | EN55011 (1991) | 130dBmV @ 150kHz* (common mode) 130dBmV @ 150kHz* (differential mode) Reducing with frequency by 20dB/decade |  |

| ### External AC Supply (RFI) Filters and AC Line Chokes Filters conform to EN55011 Class A conducted emission limits when used with 300m of screened motor cable and the specified 3% minimum AC Line Choke. For use on earth referenced (TN) and non-earth referenced (IT) supplies. CT = Constant Torque, HVAC = Quadratic Torque |  |  |  |  |
| --- | --- | --- | --- | --- |
| 584SV Type | Rating | No. of CO464517 Filters Required in Parallel * | Total Filter Watt Loss | AC Line Choke |
| Type 8 (90kW) Type 8 (110kW) Type 8 (132kW) Type 9 (160kW) Type 9 (180kW) Type 9 (200kW) Type 10 (250kW) Type 10 (280kW) | CT + HVAC CT + HVAC CT + HVAC CT + HVAC CT + HVAC CT + HVAC CT + HVAC CT + HVAC | One One One Two Two Two Two Two | 50W 50W 50W 100W 100W 100W 100W 100W | CO389936U201 CO389936U201 CO389936U201 CO389936U202 CO389936U202 CO389936U202 CO389936U203 CO389936U203 |

| ### AC Line Choke Specification |  |  |  |  |
| --- | --- | --- | --- | --- |
| Type 8, 9 and 10 Inverters require the use of an AC Line Choke, however, where an Inverter is individually supplied from a dedicated transformer with the required impedance, the AC Line Choke is not required. Where a system comprises a number of Type 8, 9 and 10 Inverters connected to a common supply, a separate AC Line Choke is required in the supply to each Inverter. When an EMC external ac supply filter is used, the AC Line Choke must be fitted between the filter and Inverter. Failure to provide the correct line impedance will severely reduce the Inverters lifetime and could result in catastrophic failure of the Inverter. The required AC Line Choke line impedance is nominally 3% of the Inverter rating for the highest power build of each frame size. Eurotherm Drives can supply the following line chokes: |  |  |  |  |
| 584SV Type | Inductance/Phase | RMS Current | Peak Instantaneous Current | Part No. |
| Type 8 | 75mH | 308A | ±1000A | CO389936U201 |
| Type 9 | 50mH | 490A | ±1600A | CO389936U202 |
| Type 10 | 35mH | 620A | ±2200A | CO389936U203 |

|  | ### External AC Supply (RFI) Filter Specification |  |  |  |
| --- | --- | --- | --- | --- |
|  | Filter Part No. | CO464517 | Voltage | 500 VAC |
|  | Humidity | 90% RH (non-condensing) | Frequency | 50/60Hz |
|  | Vibration | 10-200Hz 1.8g | Current | 340A @ 50°C |
|  | Weight | 13kg approximately | Leakage Current | 2A @ 440V 50Hz |
|  | Terminals | 35 x3mm bus bar (M12 fixings) | Surge | 3kV 1.2/50ms |
|  | Filter Mounting | 4 x M10 | Electric Strength | 2700VDC/1 minute |

| ### Brake Unit Rating Type 8, 9 and 10 brake units have the following specification: Maximum braking power: 150% Operating voltage: 750 - 820V dc Maximum duty cycle: 30% Maximum on time: 20 Seconds |  |  |
| --- | --- | --- |
| 584SV Type | Maximum Brake Current @750V dc | Minimum Brake Resistance |
| Type 8 (90kW) | 220A | 3.40 ohms |
| Type 8 (110kW) | 264A | 2.84 ohms |
| Type 8 (132kW) | 300A | 2.50 ohms |
| Type 9 (160kW) | 360A | 2.00 ohms |
| Type 9 (180kW) | 440A | 1.70 ohms |
| Type 9 (200kW) | 450A | 1.60 ohms |
| Type 10 (250kW) | 525A | 1.43 ohms |
| Type 10 (280kW) | 675A | 1.11 ohms |

| ### Main Cooling Fan and Supply Requirements Type 8 & 9 Inverters have an integral main cooling fan, but the Type 10 Inverter has a separate main cooling fan. Refer to drawing HG463009G001 at the back of this book. All the Inverter types require an external single phase supply and fuse protection (motor start type) for the main cooling fan. |  |  |  |
| --- | --- | --- | --- |
| 584SV Type | Type 8 | Type 9 | Type 10 |
| Supply Voltage | 110 to 130V ac, 50/60 Hz |  |  |
| Fuse Rating | 3A | 6A | 10A |
| Supply Voltage | 220 to 240V ac, 50/60Hz |  |  |
| Fuse Rating | 2A | 4A | 6A |
| Airflow Requirement | 750m3/h (425CFM) | 1200m3/h (700CFM) | 1700m3/h (1000CFM) |

|  |  | ### Supply Harmonic Analysis Assumptions: 18,000A short circuit supply capability, constant torque load and stated nominal motor output power. where Q1n is the rated rms value of the fundamental voltage of the supply transformer. The results conform to stage 3 of the Engineering Recommendation G.5/3 September 1976, Classification ‘C’: Limits for Harmonics in the UK Electricity Industry. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Drive Type |  | 584SV |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | Type |  | 8 |  |  | 8 |  |  | 8 |  | 9 |  | 9 |  | 9 |  | 10 |  | 10 |
|  |  |  | Motor Power (kW) |  | 90 |  |  | 110 |  |  | 132 |  | 160 |  | 180 |  | 200 |  | 250 |  | 280 |
|  |  |  | Fundamental Voltage (V) |  | 400 |  |  | 400 |  |  | 400 |  | 400 |  | 400 |  | 400 |  | 400 |  | 400 |
|  |  |  | Typical Motor Efficiency |  | 93% |  |  | 93% |  |  | 93% |  | 94% |  | 94% |  | 94% |  | 95% |  | 95% |
|  |  | Harmonic No. |  | RMS Current (A) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | 1 |  | 141.3 |  |  | 172.1 |  | 209.2 |  |  | 246.8 |  | 274.2 |  | 325.1 |  | 360.9 |  | 416.9 |  |
|  |  | 5 |  | 67.2 |  |  | 74.9 |  | 80.0 |  |  | 99.5 |  | 102.9 |  | 114.8 |  | 130.0 |  | 141.8 |  |
|  |  | 7 |  | 32.3 |  |  | 32.4 |  | 29.3 |  |  | 39.1 |  | 36.9 |  | 37.8 |  | 44.1 |  | 44.5 |  |
|  |  | 11 |  | 10.4 |  |  | 12.3 |  | 14.8 |  |  | 17.5 |  | 19.3 |  | 22.0 |  | 24.9 |  | 27.4 |  |
|  |  | 13 |  | 6.5 |  |  | 6.8 |  | 7.2 |  |  | 8.9 |  | 9.3 |  | 10.8 |  | 12.1 |  | 13.7 |  |
|  |  | 17 |  | 4.7 |  |  | 5.5 |  | 6.2 |  |  | 7.6 |  | 8.1 |  | 8.9 |  | 10.2 |  | 10.7 |  |
|  |  | 19 |  | 2.8 |  |  | 3.2 |  | 3.9 |  |  | 4.6 |  | 5.2 |  | 6.1 |  | 6.9 |  | 7.8 |  |
|  |  | 23 |  | 2.6 |  |  | 2.9 |  | 3.1 |  |  | 3.9 |  | 4.0 |  | 4.2 |  | 4.9 |  | 4.9 |  |
|  |  | 25 |  | 1.7 |  |  | 2.1 |  | 2.5 |  |  | 2.9 |  | 3.3 |  | 3.8 |  | 4.3 |  | 4.6 |  |
|  |  | 29 |  | 1.6 |  |  | 1.7 |  | 1.7 |  |  | 2.2 |  | 2.2 |  | 2.3 |  | 2.7 |  | 2.8 |  |
|  |  | 31 |  | 1.1 |  |  | 1.4 |  | 1.6 |  |  | 2.0 |  | 2.1 |  | 2.3 |  | 2.7 |  | 2.7 |  |
|  |  | 35 |  | 1.0 |  |  | 1.1 |  | 1.0 |  |  | 1.3 |  | 1.4 |  | 1.6 |  | 1.8 |  | 2.0 |  |
|  |  | 37 |  | 0.8 |  |  | 1.0 |  | 1.0 |  |  | 1.3 |  | 1.3 |  | 1.4 |  | 1.7 |  | 1.7 |  |
|  | Total RMS Current (A)* |  |  | 160.5 |  | 191.5 |  |  |  | 227.0 |  | 271.0 |  | 297.0 |  | 348.0 |  | 387.5 |  | 444.0 |  |
|  | THD (V) % |  |  | 2.6 |  | 2.9 |  |  |  | 3.1 |  | 3.9 |  | 3.9 |  | 4.3 |  | 4.7 |  | 4.9 |  |

*These figures are different to those stated in the Electrical Ratings -Power Circuit (constant torque) table due to the difference in assumed operating conditions.