|  | 584SV Series Frequency Inverter - HA463660 |  |
| --- | --- | --- |
|  | Chapter | 7 |
|  | Trips and Fault Finding |  |
|  | Contents Page |  |

- Trips

- What Happens when a Trip Occurs

- Inverter Indications

- Fault Finding

# Trips and Fault Finding

## Trips

### What Happens when a Trip Occurs

#### Inverter Indications

In addition to the diagnostics provided by the Operator Station, eight fault LEDs are situated on the Power Control Board to provide an indication for the cause of fault trips. The fault LEDs are visible when the bottom terminal cover is removed - refer to Figure 2-1.

| Fault | Illuminated LED’s |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| M1 phase overcurrent |  | “ |  |  |  |  |  |  | Œ |
| M2 phase overcurrent |  | “ |  |  |  |  |  |  |  |
| M3 phase overcurrent |  | “ |  |  |  |  | Ž |  |  |
| M1 phase IGBT fault alarm |  |  |  |  |  |  |  |  | Œ |
| M2 phase IGBT fault alarm |  |  |  |  |  |  |  |  |  |
| M3 phase IGBT fault alarm |  |  |  |  |  |  | Ž |  |  |
| DB unit IGBT fault alarm |  |  |  |  |  |  |  |  |  |
| M1 phase IGBT over-temperature |  |  |  | ‘ |  |  |  |  | Œ |
| M2 phase IGBT over-temperature |  |  |  | ‘ |  |  |  |  |  |
| M3 phase IGBT over-temperature |  |  |  | ‘ |  |  | Ž |  |  |
| DB unit IGBT over-temperature |  |  |  | ‘ |  |  |  |  |  |
| L1 thermostat over-temperature |  |  | ’ |  |  |  |  |  | Œ |
| L2 thermostat over-temperature |  |  | ’ |  |  |  |  |  |  |
| L3 thermostat over-temperature |  |  | ’ |  |  |  | Ž |  |  |
| AC supply fail |  | “ |  |  |  |  |  |  |  |
| Output current imbalance |  |  |  | ‘ |  |  |  |  |  |
| CAL board not fitted |  | “ | ’ | ‘ |  |  |  |  |  |
| Internal supply fail |  | “ | ’ |  |  |  |  |  |  |
| FPGA not programmed |  | “ | ’ | ‘ |  |  | Ž |  | Œ |

Figure 7-1  LED Fault Indications

## Fault Finding

| Fault | Remedy |
| --- | --- |
| M1 phase overcurrent | Output current greater than trip level. Check output wiring |
| M2 phase overcurrent | and motor for insulation breakdown or short-circuits either |
| M3 phase overcurrent | between phases or between phase and earth. |
| M1 phase IGBT fault alarm | Excessive output current. |
| M2 phase IGBT fault alarm | Maximum IGBT junction temperature exceeded - check |
| M3 phase IGBT fault alarm | main cooling fan. |
| DB unit IGBT fault alarm | Check wiring and verify value of brake resistor. |
| M1 phase IGBT over-temperature | Maximum IGBT junction temperature exceeded. |
| M2 phase IGBT over-temperature | Check operation of main cooling fan and supply. |
| M3 phase IGBT over-temperature | Check that cooling path is free from obstruction. |
| DB unit IGBT over-temperature | Clean or replace cubicle inlet air filters. |
| L1 thermostat over-temperature | Maximum input bridge temperature exceeded. |
| L2 thermostat over-temperature | Check that motor load is within drive rating. |
| L3 thermostat over-temperature | Check value of AC line choke. Maximum internal temperature exceeded. Check that all fans are operational. |
| AC supply fail | One or more supply phases missing - check supply wiring. |
| Output current imbalance | Check wiring to motor and motor itself for earth faults. |
| CAL board not fitted | Internal fault - consult supplier |
| Internal supply fail | Internal fault - consult supplier |
| FPGA not programmed | Internal fault - consult supplier |

Figure 7-2  Fault Finding